## Step 1
Infection Control Risk Assessment
Matrix of Precautions for Construction and Renovation
Step One:
Using the following table, identify the Type of Construction Project Activity (Type A-D)
Inspection and non-invasive activities.
Includes, but is not limited to:
TYPE A | - removal of ceiling tiles for visual inspection limited to 1 tile per 50 square feet
- painting (but not sanding)
- wallcovering, electrical trim work, minor plumbing, and activities which do not generate dust or require cutting of walls or access to ceilings other than for visual inspection.
Small scale, short duration activities which create minimal dust
Includes, but is not limited to:
TYPE B | - installation of telephone and computer cabling
- access to chase spaces
- cutting of walls or ceiling where dust migration can be controlled.
Work that generates a moderate to high level of dust or requires demolition or removal of any fixed building components or assemblies
Includes, but is not limited to:
TYPE C | - sanding of walls for painting or wall covering
- removal of floorcoverings, ceiling tiles and casework
- new wall construction
- minor duct work or electrical work above ceilings
- major cabling activities
Major demolition and construction projects
Includes, but is not limited to:
TYPE D | - activities which require consecutive work shifts
- requires heavy demolition or removal of a complete cabling system
- new construction

## Step 2
PATIENT RISK GROUP MATRIX
Step Two:
Using the following table, Identify the Patient Risk Groups that will be affected.
If more than one risk group will be affected, select the higher group:
Low Risk
- Non-Patient Care Offices
- General Traffic Areas
Medium Risk
- Patient Care Offices (Including patient waiting areas)
- Supply, Medication or Equipment Storage Areas (Related to Patient Care)
- Non-invasive Outpatient Diagnostic Study Areas ( examples outpatient breast imaging, outpatient CT areas, outpatient MRI areas, outpatient echocardiography)
- Outpatient Treatment Areas Not Caring for Immunocompromised Patients (example outpatient physical therapy areas)
High Risk
- All Inpatient Care Units (adult and pediatric)
- Clinical Laboratories (to protect specimen integrity)
- Pharmacy (all compounding areas)
- Sterile Processing, Sterile Storage
- Linen Storage
- Emergency Department
Highest Risk
- Intensive Care Units (all)
- Operating Rooms (all, including outpatient, labor and delivery)
- Invasive Diagnostic Procedure Areas (CVIR, Cath Lab, Endoscopy, Bodine Center)
- Bone Marrow Transplant Unit
- Inpatient and Outpatient Oncology Areas

## Step 3
Step Three: Match the
Patient Risk Group (Low, Medium, High, Highest) with the planned…
Construction Project Type (A,B,C,D) on the following matrix to find the…
Class of Precautions (I,II,IIIor IV) or level of infection control activities required.
Class I-IV Precautions are delineated on the following page.
IC Matrix - Class of Precautions: Construction Project by Patient Risk
Construction Project Type
Patient Risk Group | TYPE A | TYPE B | TYPE C | TYPE D
LOW Risk Group | I | II | II | III/IV
MEDIUM Risk Group | I | II | III | IV
HIGH Risk Group | I | II | III/IV | IV
HIGHEST Risk Group | II | III/IV | III/IV | IV

## Step 4
Description of Required Infection Control Precautions by Class
| During Construction Project | Upon Completion of Project
Class I | 1. Execute work by methods to minimize raising dust from construction operations.
2. Immediately replace a ceiling tile displaced for visual inspection.
Class II | 1. Provide active means to prevent airborne dust from dispersing into atmosphere. | 1. Wipe work surfaces with disinfectant.
2. Contain construction waste before transport in tightly covered containers.
2. Water mist work surfaces to control dust while cutting.
3. Wet mop and/or vacuum with HEPA filtered vacuum before leaving work area.
3. Seal unused doors with duct tape.
| 4. Block off and seal air vents. | 4. Remove isolation of HVAC system in areas where work is being performed.
5. Place dust mat at entrance and exit of work area.
6. Remove or isolate HVAC system in areas where work is being performed.
Class III | 1. Remove or isolate HVAC system in area where work is being done to prevent contamination of duct system. | 1. Do not remove barriers from work area until completed project is inspected by the owner's Facilities Design and Construction Department and thoroughly cleaned by the owner's Environmental Services Department.
2. Complete all critical barriers, i.e., sheetrock, plywood, plastic, to seal area from non work area or implement control cube method (cart with plastic covering and sealed connection to work site with HEPA vacuum for vacuuming prior to exit) before construction begins.
2. Remove barrier materials carefully to minimize spreading of dirt and debris associated with construction.
| 3. Maintain negative air pressure within work site utilizing HEPA equipped air filtration units. | 3. Vacuum work area with HEPA filtered vacuums.
4. Wet mop area with disinfectant.
| 4. Contain construction waste before transport in tightly covered containers. | 5. Remove isolation of HVAC system in areas where work is being performed.
5. Cover transport receptacles or carts. Tape covering unless solid lid.
Class IV | 1. Isolate HVAC system in area where work is being done to prevent contamination of duct system. | 1. Do not remove barriers from work area until completed project is inspected by the owner's Facilities Design and Construction Department and thoroughly cleaned by the owner's Environmental Services Department.
2. Complete all critical barriers, i.e., sheetrock, plywood, plastic, to seal area from non work area or implement control cube method (cart with plastic covering and sealed connection to work site with HEPA vacuum for vacuuming prior to exit) before construction begins.
2. Remove barrier material carefully to minimize spreading of dirt and debris associated with construction.
| 3. Maintain negative air pressure within work site utilizing HEPA equipped air filtration units. | 3. Contain construction waste before transport in tightly covered containers.
| 4. Seal holes, pipes, conduits, and punctures appropriately. | 4. Cover transport receptacles or carts. Tape covering unless solid lid.
| The following may be required. This will be determined by the patient risk group. | 5. Vacuum work area with HEPA filtered vacuums.
6. Wet mop area with disinfectant.
| 5. Construct anteroom and require all personnel to pass through this room so they can be vacuumed using a HEPA vacuum cleaner before leaving work site or they can wear cloth or paper coveralls that are removed each time they leave the work site. | 7. Remove isolation of HVAC system in areas where work is being performed.
6. All personnel entering work site are required to wear shoe covers. Shoe covers must be changed each time the worker exits the work area.

## Negative Air Calculation
Determining Work Area Ventilation Requirements
Use this chart to determine number of negative air units required.
Square footage of work area | 253
Height of work area (In feet)
Number of air changes per hour | 4
( 4 is default)
Capacity of negative air unit | 2000 | 1800
( 2000 cfm is default)
Number of units needed | 0.4