# IS TELECOMMUNICATION CLOSET REQUIREMENTS

## Revised by Robert Squillace March27, 2008

-Minimal IDF closet dimensions 10’ X 10’ preferred.

-1/2” Plywood on all four walls and paint black

-Provide drop ceiling 10’-12’ high.

-Provide overhead lighting.

-Install (2) dedicated emergency quad outlets (1 for voice/ 1 for data) at 18” height. (Locations TBD by IS staff.) Quantity of outlets subject to change.

-Install (2) dedicated emergency NEMA L6-30P (30 Amp twist, 208V) Install at 18” height behind data rack or within data cabinet. (Locations TBD by IS staff.)

-Provide tile floor.

-Provide AC based on equipment specifications and BTU output.

(NOTE- Temperature range should be 18 degrees Celsius to 24 degrees Celsius (64-75 degrees Fahrenheit). The humidity range should be 30-55% relative humidity.

-Provide grounding bar.

-Entrance door to open out, and be equipped with an electronic proxy reader from Siemens, along with bypass key cored with a TJU/H Secure key. (IS will specify)

TJU Security Department to set up individual access and monitor.

-(4) 4” floor cores or overhead pathway are required for voice and data copper/fiber optic riser connectivity. Building location and ownership, existing pathways, and existing closet locations will determine coring vs. overhead pathway.

-(4) 4” sleeves are required above the drop ceiling, through closet walls, for voice/data station cable entrance pathway. (12” wide cable tray to be installed by TCOM contractor).

- New closet shall be dedicated to voice/data equipment and cabling only. However, in certain instances, this closet may be shared with other low voltage cabling and systems such as: CATV, Audio/Video and Security Systems. High Voltage panels/equipment, running water, custodial, transportation, or storage by others is prohibited. Closet must be accessible by TJU/H Information Systems staff 24 hours a day/ 7 days per week.